## Slide 1: Modbus testing procedure

## Slide 2: Modbus testing Procedure
Prerequisite
  Modscan software
  RS485 to USB convertor with driver installed in computer
  Modbus device (address list)
Procedure
  Set the computer port as same as Modbus device and note the port number (from device manager0
  Open Modscan software
  Connect Modscan with device
  Set the port as noted at step ‘1’
  Configure the setting as same as Modbus device
  Set the device ID and register address based on Modbus manual
  Monitor the value and response value

## Slide 3: 1) Go to Control Panel to check the port number and configuration

## Slide 4: 2) Go to device manager

## Slide 5: 3) Right Click on USB

## Slide 6: 4) Check the configuration and take note the port number

## Slide 7: 6) Open ModScan12

## Slide 8: 7) Initiate the connect
This setting must be as same as Modbus device and port configuration

## Slide 9: 7) Set Device ID, Point type and Register address
This number will increase once communication is up
The value could be absolved
Device ID is ‘1’
Register address from 30001 to 20020 (this information will get form Modbus device manufacturer
Point type

## Slide 10: 8) Set Device ID, Point type and address and check the com status